COLUMBUS FIRE DEPARTMENT

1101 JACKSON STREET

COLUMBUS, INDIANA  47201

(812) 376-2679

(812)-376-2568- FAX

JAMES D. LIENHOOP, MAYOR		   		       MIKE COMPTON, FIRE CHIEF

PRE-INSPECTION FIRE CHECKSLIST

Fire inspectors look at many items in your place of business. So that you may have a better understanding of what to keep an eye on, in regards to maintenance and safety, we have provided the following checklist.

EXITS

Door/aisle is not obstructed.

Proper lock/hardware on the exit. (No flush bolts, hasps, etc.)

Exit doors open easily.

There is a sign over the main entrance, “This door is to remain unlocked during business hours,” if the door has a double-keyed deadbolt.

Illumination exit signs maintained in working order.

Means of egress shall be kept clear.

Emergency lights maintained and in working order.

Doors with panic hardware shall have no other locking devices.

Maximum occupancy signage shall be posted in a conspicuous location near the main entrance for assembly occupancies.

EXTENGUSIHER/FIRE PROTECTION EQUIPMENT

Minimum 2A10BC extinguisher(s) installed.

Extinguishers have been serviced within the past year and a new service tag is attached.

Extinguishers are securely mounted or in an approved cabinet.

Fire extinguisher not obstructed.

Fire extinguishers top does not exceed 5 feet from floor when mounted.

Hood extinguishing system maintained, and six month service and cleaning documented.

Class K extinguisher installed 10-20 feet from hood and duct system.

Fire alarm system is in proper working order- system tested annually- record of testing.

18 inches of clearance between storage and sprinkler heads.

Sprinkler system shall be maintained and tested annually.

Standpipe shall be tested every 5 years.

APPLIANCE/MECHANICAL

No propane used/stored in building.

All appliances are properly connected and vented.

ELECTRICAL

No extension cords in use in place of permanent wiring.

There are no spliced or frayed cords/ wires.

Spacer(s) in electrical panel gap(s) provided.

No broken or faulty switch/outlets.

No exposed wire in conduit.

No missing/broken electrical cover plate(s).

Electrical panel is not overloaded/ obstructed.

No multi-plug adapters in use, other than approved power strips.

Circuit breakers are labeled.

Electrical cords do not extend through walls, ceilings and floors, or under doors or floor coverings.

30 inches of clearance maintained in front of electrical panels.

STORAGE/ COMBUSTIBLE MATERIAL/ HOUSEKEEPING

Flammable liquid properly stored.

Oil rags in non-combustible container with lid.

“No Smoking” signs installed as required.

No combustible material stored near ignition source.

Maintain clear and visible access to and around fire department connection.

No accumulation of combustible materials.

Compressed gas cylinders secured.

Area around building free of combustible materials.

No storage shall be kept in exit stairways.

Fire and smoke walls shall be maintained and have no opening other than those allowed by code.

MISCELLANEOUS

Fire lanes shall be approved by fire department.

Address numbers shall be posted in contrasting colors on the front and rear doors for commercial businesses and shall be 8 inches on the front door, and 4 inches on the back door. All other structures shall be 4 inches except home daycares, which shall be 6 inches.

Rapid key entry box maintained by property owner.

Charcoal grills, propane grills and/ or other open-flame cooking devices shall not be located on combustible balconies or within 10 feet of combustible construction.EXCEPTIONS:1) One and two family dwellings, and 2) Where balconies/decks are protected by an automatic sprinkler system.

Note: This list is a general guideline only for common violations that can be readily determined by the occupant.

# Text boxes

HOME OF THE FIRST DIESEL

FIRE ENGINE

IN 1939